## Site Power Dimensioning
Telecom Site Power Dimensioning Model (-48V DC System)
Scenario 1: VRLA battery site, 60 A load, 6 h backup. Change the yellow cells to size any site.
INPUTS | Value | Unit / Note | Standard cable sizes (mm2)
DC load current | 60 | A | 16
Nominal voltage | 48 | V | 25
Backup time | 6 | hours | 35
Depth of Discharge (DoD) | 0.8 | VRLA typical 0.8; lithium 0.9 | 50
Ageing factor | 1.25 | battery ageing margin | 70
Temperature factor | 1 | 1.0 normal; 1.1 for hot sites | 95
Charging current factor | 0.1 | 0.1 = 0.1C | 120
Rectifier module rating | 50 | A per module | Source: typical standard sizes; confirm with ampacity tables / customer spec.
Rectifier efficiency | 0.96 | 0.96 = 96%
AC voltage (single phase) | 230 | V | LEGEND
AC power factor | 0.99 | rectifier input PF | Yellow cells, blue text = inputs (edit these)
Extra AC load (AC, lights) | 3 | kW | Green cells = final design results
DG margin | 0.2 | 0.2 = 20% growth margin | Other cells = formulas (do not edit)
DG power factor | 0.8 | typical 0.8
Cable length (one way) | 10 | m
Allowed voltage drop | 1 | V (about 2% of 48V)
Copper resistivity | 0.0175 | ohm-mm2/m
CALCULATIONS | Result | Meaning
DC load power (kW) | 2.88 | P = V x I
Basic battery capacity (Ah) | 360 | Load x hours
Required battery (Ah) | 562.5 | Corrected for DoD, ageing, temperature
Standard battery size (Ah) | 600 | Next standard size (100 Ah steps)
Battery charging current (A) | 60 | Charging factor x battery Ah
Total rectifier current (A) | 120 | Load + battery charging
Modules needed | 3 | Rounded up to whole modules
Modules with N+1 | 4 | One extra module for redundancy
Installed rectifier capacity (A) | 200 | Total rectifier capacity
DC output power (kW) | 5.76 | Rectifier output at full load + charging
AC input power (kW) | 6 | After rectifier efficiency
AC input current (A) | 26.3505 | I = P / (V x PF)
AC breaker size (A) | 40 | 1.25 x current, rounded to 10 A steps
Total AC load (kW) | 9 | Rectifier input + extra AC load
Load with margin (kW) | 10.8 | Growth margin added
DG required (kVA) | 13.5 | kVA = kW / PF
Standard DG size (kVA) | 15 | Next standard size (5 kVA steps)
DC cable area required (mm2) | 42 | Area = rho x 2L x I / Vdrop
Standard cable size (mm2) | 50 | Next size from table (check ampacity separately)
FINAL DESIGN SUMMARY
DC load | 60 A / 2.9 kW at -48V DC
Battery bank | 600 Ah, -48V
Rectifier | 4 x 50 A modules (N+1)
AC input breaker | 40 A
DG set | 15 kVA
DC cable (rectifier to DCDB) | 50 mm2 copper

## Scenario 2 Lithium
Scenario 2: Lithium Battery Site (Hot Location)
Scenario 2: Lithium battery (DoD 0.9), 40 A load, 4 h backup, temperature factor 1.1.
INPUTS | Value | Unit / Note | Standard cable sizes (mm2)
DC load current | 40 | A | 16
Nominal voltage | 48 | V | 25
Backup time | 4 | hours | 35
Depth of Discharge (DoD) | 0.9 | VRLA typical 0.8; lithium 0.9 | 50
Ageing factor | 1.1 | battery ageing margin | 70
Temperature factor | 1.1 | 1.0 normal; 1.1 for hot sites | 95
Charging current factor | 0.1 | 0.1 = 0.1C | 120
Rectifier module rating | 50 | A per module | Source: typical standard sizes; confirm with ampacity tables / customer spec.
Rectifier efficiency | 0.96 | 0.96 = 96%
AC voltage (single phase) | 230 | V | LEGEND
AC power factor | 0.99 | rectifier input PF | Yellow cells, blue text = inputs (edit these)
Extra AC load (AC, lights) | 3 | kW | Green cells = final design results
DG margin | 0.2 | 0.2 = 20% growth margin | Other cells = formulas (do not edit)
DG power factor | 0.8 | typical 0.8
Cable length (one way) | 10 | m
Allowed voltage drop | 1 | V (about 2% of 48V)
Copper resistivity | 0.0175 | ohm-mm2/m
CALCULATIONS | Result | Meaning
DC load power (kW) | 1.92 | P = V x I
Basic battery capacity (Ah) | 160 | Load x hours
Required battery (Ah) | 215.1111 | Corrected for DoD, ageing, temperature
Standard battery size (Ah) | 300 | Next standard size (100 Ah steps)
Battery charging current (A) | 30 | Charging factor x battery Ah
Total rectifier current (A) | 70 | Load + battery charging
Modules needed | 2 | Rounded up to whole modules
Modules with N+1 | 3 | One extra module for redundancy
Installed rectifier capacity (A) | 150 | Total rectifier capacity
DC output power (kW) | 3.36 | Rectifier output at full load + charging
AC input power (kW) | 3.5 | After rectifier efficiency
AC input current (A) | 15.3711 | I = P / (V x PF)
AC breaker size (A) | 20 | 1.25 x current, rounded to 10 A steps
Total AC load (kW) | 6.5 | Rectifier input + extra AC load
Load with margin (kW) | 7.8 | Growth margin added
DG required (kVA) | 9.75 | kVA = kW / PF
Standard DG size (kVA) | 10 | Next standard size (5 kVA steps)
DC cable area required (mm2) | 24.5 | Area = rho x 2L x I / Vdrop
Standard cable size (mm2) | 25 | Next size from table (check ampacity separately)
FINAL DESIGN SUMMARY
DC load | 40 A / 1.9 kW at -48V DC
Battery bank | 300 Ah, -48V
Rectifier | 3 x 50 A modules (N+1)
AC input breaker | 20 A
DG set | 10 kVA
DC cable (rectifier to DCDB) | 25 mm2 copper

## Charts
Visualization of Power Dimensioning Results
All chart data below is linked by formula to the model sheets, so charts update when you change the yellow input cells.
Chart 1: Scenario 1 vs Scenario 2 (key design sizes)
Item | Scenario 1 (VRLA) | Scenario 2 (Lithium)
Battery (Ah) | 600 | 300
Installed rectifier (A) | 200 | 150
AC breaker (A) | 40 | 20
DG set (kVA) | 15 | 10
DC cable (mm2) | 50 | 25
Chart 2: Required battery capacity vs backup time
Backup time (h) | Scenario 1 required Ah | Scenario 2 required Ah
1 | 93.75 | 53.7778
2 | 187.5 | 107.5556
3 | 281.25 | 161.3333
4 | 375 | 215.1111
5 | 468.75 | 268.8889
6 | 562.5 | 322.6667
7 | 656.25 | 376.4444
8 | 750 | 430.2222
9 | 843.75 | 484
10 | 937.5 | 537.7778
11 | 1031.25 | 591.5556
12 | 1125 | 645.3333
Chart 3: Rectifier requirement vs DC load (Scenario 1 settings)
DC load (A) | Battery std (Ah) | Total rectifier current (A) | Installed capacity N+1 (A)
20 | 200 | 40 | 100
30 | 300 | 60 | 150
40 | 400 | 80 | 150
50 | 500 | 100 | 150
60 | 600 | 120 | 200
70 | 700 | 140 | 200
80 | 800 | 160 | 250
90 | 900 | 180 | 250
100 | 1000 | 200 | 250
Chart 4: DG set load breakdown (Scenario 1)
Component | kW
Rectifier AC input | 6
Extra AC load (AC, lights) | 3
Growth margin | 1.8
Chart 5: Rectifier DC output split (Scenario 1)
Component | kW
Telecom load | 2.88
Battery charging | 2.88
Chart 6: DC cable area vs cable length (Scenario 1)
Length one way (m) | Required area (mm2)
5 | 21
10 | 42
15 | 63
20 | 84
25 | 105
30 | 126

## Notes
NOTES AND ASSUMPTIONS
Purpose | Excel model to size battery, rectifier, AC breaker, DG set and DC cable for a telecom site.
Important | All input values are typical/illustrative. Real projects follow customer specifications and vendor datasheets.
FORMULAS USED
DC power | P = V x I
Battery capacity (Ah) | Load current x backup hours / DoD x ageing factor x temperature factor, then next standard size
Rectifier current | Load current + battery charging current (charging factor x battery Ah)
Rectifier modules | ROUNDUP(total current / module rating), plus 1 module for N+1 redundancy
AC input power | DC output power / rectifier efficiency
AC input current | I = P / (V x PF), single phase
AC breaker | 1.25 x AC input current, rounded up to 10 A steps
DG kVA | (Rectifier AC input + extra AC load) x (1 + margin) / DG power factor, rounded to 5 kVA steps
DC cable area | Area = resistivity x 2 x length x current / allowed voltage drop
REFERENCES
Battery sizing standard | IEEE 485 (lead-acid battery sizing). Confirm method with customer standard.
Cable | Standard size from table only checks voltage drop. Also check cable ampacity from standard tables.
Charging factor | 0.1C is a typical VRLA assumption; lithium batteries may allow higher rates (check datasheet).
Resistivity | Copper 0.0175 ohm-mm2/m (typical value at about 20 C).
HOW TO USE | Edit only yellow input cells (blue text). Results update automatically. Use the Scenario 2 sheet as a second example.